Utilisation of Straw and Wood in Large-Scale Power Plants.

Ph.D. Per Ottosen, Energi E2 A/S, DK- Copenhagen.

Abstract:

Each year 300.000 tons of wood pellets are to be combusted at Avedøre Unit 2, corresponding to a typical monthly use of 40000-60000 t, as biomass only are used in the cold part of the year. At the same plant up to 150000 tons of straw in bales are combusted in a separate grate fired boiler.

Avedøre Unit 2 consist of a 100 MWt straw fired boiler, two 50 MWe gas turbines, and an 800 MWt tower boiler. The two boilers and the gas turbines are integrated into the same water/steam cycle. The exhaust gas from the gas turbines are used for feed water preheating. The steam produced in the straw fired boiler is mixed with the steam produced in the tower boiler and enter the high pressure turbine. The unit is designed for steam at 580 °C/600 °C and 300 bars. The main boiler is fired with a mix of wood pellets, natural gas and heavy fuel oil and is a once through of the Benson type with single reheat. The Furnace is designed for coal firing and has a tangential firing system consisting of 16 low NOx burners placed at the corners of the furnace in four levels. Initially the steam temperature has been reduced to 540 °C and 70 % load to reduce the corrosion rate caused by introducing the wood pellets

The boiler is equipped with deNOx unit. However, during the introduction of wood pellets 2 of the 3 layers of catalysts were removed due to expected deactivation of the catalyst.

Avedøre unit 2

Avedøre 2 is build by i/s Avedøre 2, a joint venture of Eastern Denmark’s power company Energi E2 and Sweden’s largest power company Vattenfall.

Vattenfall owns 40 per cent of the new plant.

The Avedøre site figure 1 , which can be seen from planes using Copenhagen’s main airport, is placed on reclaimed land in Køge Bay, about 10 km south of Copenhagen.

Avedøre unit 2 is placed alongside Avedøre unit 1.

Avedøre unit 1 and 2 produces electricity for eastern Denmark and heat for metropolitan region of Copenhagen. The district heating system in the metropolitan region of Copenhagen is one of Northern Europe’s largest district heating networks.

Fig. 1 Avedøre site near Copenhagen

Avedøre  unit 2 placed near the city of Copenhagen  started commercial operation at the end of 2001, and is one of the world’s most efficient, fuel flexible, and environmentally optimal CHP plants. The plant can with high efficiency burn natural gas, bio fuels as straw and wood pellets and heavy fuel oil.

The basic idea of the multifuel concept is shown on figure 2. Each fuel is burnt separately in combustion systems optimised for the fuel in order to achieve maximum efficiency for each fuel.

Therefore the fuels are not blended and burned in a combined boiler but straw is burned separately in biomass boiler, gas/oil/wood pellets is burned in a boiler constructed to pulverized fuel oil and natural gas is used in gas turbines.

Steam output from each fuel source is integrated and fed to a single modern high efficiency steam turbine.

Exhaust heat from gas turbines are used for feed water reheating.

Fig. 2 Avedøre unit 2 process diagram

The heart of Avedøre 2 is a large ultra super critical (USC) plant originally prepared to burn natural gas and heavy fuel oil. This USC plant consists of a boiler, a steam turbine, an electrical generator and a flue gas cleaning system.

Fig. 3 shows the USC boiler, steam turbine, gas turbine and flue gas cleaning lay out.

Fig.3 Lay out AVV unit 2

In order to be able to burn more biomass it was decided to retrofit the plant to burn wood pellets. This retrofit consists of three new mills for wood pellets, made as modified coal mills.

Also new pellets storage was established and a covered fuel transport system was established.

The amount of wood pellets account for 300,000 ton per year, and the remaining fuels are natural gas and heavy fuel. The plant will be able to use wood pellets from late 2002.

Figure 4 shows the handling system for wood pellets.

Fig. 4   Fuel handlings system wood pellets at AVV2

- USC plant

At the heart of Avedøre 2 is a large ultra supercritical (USC) plant burning mainly gas, oil and wood pellets. This USC plant consists of boiler, steam turbine, electrical generator and flue gas cleaning unit. The amount of wood pellets account for 300000 t per year, the remaining fuels are natural gas and heavy fuel oil. The boiler is a tangentially fired tower boiler with single reheat.

The USC plant can both produce electricity and district heat.

The USC plant is equipped with high dust SCR deNOx and ESP for dust removal and at last gypsum producing flue gas cleaning system.

- Gas turbine plant

There are two areoderivative gas turbines, which provide peak load electricity generation and which also are used to preheat the feed water to the USC boiler via exhaust heat recovery units.

The gas turbines can only burn natural gas

- Biomass plant

A biomass boiler plant, initially running on straw and with possibility of later to use wood chips, will provide additional steam to the steam turbine of the USC plant.

The biomass plant will account for about 10 per cent of annual fuel consumption at Avedøre 2, consuming 150000 t straw delivered in big bales.

Main process data of Avedøre 2:

High pressure steam 		300 bar and 580 C

Reheated steam			600 C

Fuel input main boiler			800 MW thermal

Fuel input straw fired boiler		105 MW thermal

Main production data of AVV2:

During full load in condensing mode there is no heat production, but the production of electrical power is totally 590 MWel with two gas turbines running and straw fired boiler running.

In full backpressure mode the production of electrical power and heat are 510MW/565 MJ/s with gas turbines straw fired boiler running.

Fuel flexibility

Table 1. Shows important fuel data for fuels used at Avedøre Unit 2.  Figure 5 shows a big bale of straw.  Each bale has a weight of 550 kg. The biomass boiler can burn 300000 bales per year. Figure On figure 6 there are some wood pellets. The diameter of a pellet is 8-10 mm and the length 10-20 mm.

Table 1: Data of fuel used at AVV2:

| Fuel | Heating value | Sulphur % | Ash % | CO2 emission kg/GJ |
| --- | --- | --- | --- | --- |
| Natural gas | 39,6 MJ/Nm³ | 0,00 | 0 | 57 |
| Fuel oil | 40,5 GJ/tons | 2,50 | 1 | 78 |
| Straw | 14,5 GJ/tons | 0,15 | 4 | 0 |
| Wood pellets | 17,5 GJ/tons | 0,10 | 1 | 0 |

Figure 5. One big bale of straw			Figure 6. Wood pellets

As a consequence of this high flexible fuel system and the multifuel plant concept it is possible depending on outer conditions as fuel prices, possibilities of deliverance and prices on heat and power to choose between the different fuels.

As an example on the flexibility the following three typical examples are possible:

It is assumed 6500 hours full load per year and both gas turbines running.

- Max use of natural gas

- Reduced use of natural gas. 300000 t wood pellets and 150000 t straw

- Min use of natural gas. Heavy fuel oil, 300000 t wood pellets and 150000 t straw and natural gas to gas turbines.

Figure 7 shows the different distributions of the fuel. It can be seen that fossile fuels still contributes to the main part of the fuel consumption.

Conclusions:

Avedøre Unit 2 is a new CHP plant using the best available techniques. This means very high fuel flexibility, high efficiency and with best available good environmental data.

The CHP plant can burn Natural gas, Heavy fuel oil and biomass as straw and wood pellets.

Avedøre Unit 2 can supply heat and power to consumers in the Copenhagen using the cheapest and environmentally optimal fuel from the mix of straw, wood pellets, natural gas and fuel oil.

# Text boxes

Copenhagen Airport

Pellets burned in 24 h

Average over the month